## Slide 1: Cross Checking of Completed Urban Mission Works (Circle Bathinda)
Presented by: SE, PWSSB Circle, Ludhiana

## Slide 2: Agenda
Methodology
Jurisdiction & Scope
Format of Scheme Data Obtained from EE
Sample Report (Physical Status)
Sample Report (Financial Status)
Conclusion
Cross Checking of Completed Urban Mission Works (Circle Bathinda)

## Slide 3: Jurisdiction & Scope
Juridiction:
Circle Bathinda (Division 1 & 2 Bathinda, Moga,Mansa & Ferozpur)
  03 schemes of Division 1, Bathinda
  10 schemes of Division 2, Bathinda
  08 schemes of Division Moga
  02 schemes of Division Mansa
  00 schemes of Division Ferozpur
Scope of Checking:
  Checking Physical Status on ground
  Financial Status
Cross Checking of Completed Urban Mission Works (Circle Bathinda)

## Slide 4: Methodology
1
Obtained scheme wise physical & financial data authenticated by EE
8
2
3
4
5
6
7
Compared scope of Agreement with actual execution on ground
Discussed reasons for major deviation in scope & actual execution, if any
Checked the locations of work executed on the ground on the completion plan
Held joint inspection of site with EE/SDE/JE and randomly checked the physical execution of various items on the ground
Took feedback from stakeholders of these localities to ascertain commissioning and running conditions
Held a brief concluding meeting at site
Moved to other scheme for similar action
Cross Checking of Completed Urban Mission Works (Circle Bathinda)

## Slide 5: Format of Scheme Data Obtained from EE
Name of work | Agency | Agg. No & date/Amount (Rs. In Lacs) | Date of Start / Completion |  | Actual Date of completion | Scope of work | Physical progress upto 31/07/18 | whether commissioned or not | Work Done | Remarks
 |  |  | Start | Completion |  |  |  |  |  | 
Detail Project Report for providing 100% Water supply scheme at Zira Town Distt. Ferozepur. | Sh. Rajesh Kumar Midha Contractor, Abohar | 2 of 2016-17 Rs. 143.13 Lacs | No.1137 dt:4/5/16 | 8/10/2016 5 Months | 31.12.16 | Zira W/s 100mm=9062m 150mm=825m connection= 1072 no. Roads= 136.50sqm | 100mm=9073m 150mm=824m 1072 No 225.21sqm | Commissioned | 120.57lac | Work completed and Final bill Paid
Detail Project Report for providing sewerage scheme in balance area Domestic House sewer connection at Zira Distt. Ferozepur. | Sh. Rajesh Kumar Midha Contractor, Abohar | 3 of 2016-17 Rs. 289.23 Lacs | No.1181 dt:6/5/16 | 5/1/2017 8 Months | 31.1.17 | Zira Sewer 200mm=6057m 300mm=779m 400mm= 475m 500mm=1224m 700mm= 152 m Connection= 783 No. Roads= 8716sqm | 200mm=7675m 300mm=753m 400mm=240m 500mm=1169m 700mm=148mtr 270 no 9212 sqm | Commissioned | 287.71 Lacs | Work completed and Final bill Paid
Detail Project Report for providing 100% Water supply scheme at Talwandi Bhai Distt. Ferozepur. | M/s Adarsh Traders, Malout. | 4 of 2016-17 Rs. 68.31 Lacs | No.1131 dt:4/5/16 | 12/10/2016 5 Months | 12/11/16 | Talwandi Bhai W/s 100mm=5120m connection= 200 No Roads= 515sqm | 100mm=5217m 200 no 963 sqm | Commissioned | 62.22 Lacs. | Work completed and Final bill Paid
Detail Project Report for providing 100% Water supply scheme at Dharamkot Town, Distt. Moga | M/s Adarsh Traders, Malout. | 5 of 2016-17 Rs. 90.99 Lacs | No.1143 dt:4/5/16 | 12/10/2016 5 Months | 12/11/16 | Dharamkot W/s 100mm=5375m 150mm=1950 m connection= 212 No. | 100mm=5486m 150mm=1935m 212 no | Commissioned | 90.10 Lacs | Work completed and Final bill Paid
Detail Project Report for providing 100% Water supply scheme at MakhuTown, Distt. Ferozpur | Sh. Gurmeet Singh Contractor | 6 of 2016-17 Rs. 71.39 Lacs | No. 1422 dt.1/6/16 15/6/16 | 14/12/16 6 months | - | Makhu W/S 100 mm= 4348 mtr 150 mm=910mtr connection= 167 No Roads =319sqm | 100mm=4347m 150mm=907m 167 no 933 sqm | Commissioned | 67.81 Lacs | Work completed and Final bill Paid
Detail Project Report for providing 100% Water supply scheme at Nihal Singh walaTown, Distt. MOGA | Sh. Rajesh Kumar Midha Contractor, Abohar | 2016-17 Rs. 197.88 Lacs | No. 2493 dt.16.9.16 | 15.1.17 4months | - | NihalSingh W/S 100 mm= 12803 mtr 150 mm=465mtr 200mm=540mtr 13808mtr connection= 500 No Roads =1556 sqm | 100mm=12759mtr 150 mm=464mtr 200mm=540mtr 13763mtr 520 Nos 2861 sqm | Commissioned | 175.36 lacs | Work completed and Final bill Paid
Detail Project Report for providing sewerage scheme in balance area Domestic sewer connection at Dharamkot Town, Distt. Moga. | M/s S R Builders & exporters Patiala | 2016-17 Rs. 130.41 Lacs | No.2327dt: 15.9.16 | 14/1/2017 4 Months | 15.03.2017 | Dharamkot Sewer 200mm=2931m 250mm=1243m, 300mm= 396m 400mm=991m Roads =3042 sqm | 200mm =2945m 250mm =905 - 400mm=949mtr 2775 sqm | Commissioned | 110.54 lac | Work completed and Final bill Paid
1. Certified that all water supply & sewerage lines are commissioned and are in running condition.
2. Certified that no gap/missing links are left.
3. Certified that there is no other completed works under urban mission in jurisdiction of this office.
Cross Checking of Completed Urban Mission Works (Circle Bathinda)

## Slide 6: Sample Report (Physical Status)
Scope Of Work | Final Progress On Completion | Report
(1) | (2) | (3)
Laying Water Supply Lines for 100% Coverage in Talwandi Bhai. 100 mm DI K-7 Pipe = 5120 m. W/ S Connections = 200 Nos. Restoration of Roads = 515 sq. m | 5217 m 200 No. 963 sq.mt. | From the completion plan, few pockets where major water supply lines were laid under this contract were selected for checking status on the ground. In the start, some streets of area opposite bus stand & behind Dhaliwal Medical Store were randomly inspected. There after Ajit Nagar (across railway line) and Sheena Colony were inspected by choosing few streets at random. The commissioning & running of water supply lines was checked by making enquiry from the residents of these streets who confirmed that the lines are in running condition. In some of the houses in these areas, the water flowing in the taps were also seen. Most of the water supply lines have been laid in the areas shown in the contract plan. It was however noticed that water connections in Sheena colony were very less the reason being less provision in DNIT & area being far away from existing tubewell resulting in low pressure. Thus there is scope to increase connection by attending the pressure problem. Most of the streets were either katcha or brick paved which have been restored after laying water supply lines.
Cross Checking of Completed Urban Mission Works (Circle Bathinda)

## Slide 7: Sample Report (Financial Status)
S.No. | Parameter | Value
i | Allotment Rate | (-) 5.26 % below DNIT
ii. | DNIT Amount (in lakhs) | 72.10
iii | Agreement No. date & amount | 4 of 2016-17 68.31
iv. | Up to Date Expenditure against DPR | 66.62
v | Work done up to final bill | 62.22
vi. | Status of Final Bill | Paid
Cross Checking of Completed Urban Mission Works (Circle Bathinda)

## Slide 8: Conclusion
Physical Status
Based on random checking, it is concluded that the work shown executed on the completion plan matches with physical status on the ground.
There are deviation in quantities of some items but most these deviations occurred due to site conditions.
There are some deviation in locations where works have been executed and marked on the DNIT plan. The reasons explained by the concerned field officers were:
    Demand of MCs.
    Scope not available at some locations marked in the DNIT plan.
    Site requirements.
There are few items which are not included in the contract agreement but have been executed at site. The reasons explained by the concerned field officers were:
    Requirement at site for better efficiency of scheme
    Required at site but inadvertently not included in DNIT
Financial Status
Final Bills have been prepared in Moga division where are bills are yet to be prepared in division 1 & 2, Bathinda.
The final expenditure is likely to be within the allotment amount.
Cross Checking of Completed Urban Mission Works (Circle Bathinda)

## Slide 9: Thank you.
Cross Checking of Completed Urban Mission Works (Circle Bathinda)